{"text_format":"2","workbook":"xls","n_sheets":5,"sheets":["실내기","싱글형","실외기","냉방전용","설치비"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"실내기","index":0,"n_rows":34,"n_cols":17,"rows_kept":34,"cut":false,"hidden":false,"merged":[[3,0,4,0],[3,1,4,1],[3,2,4,2],[3,3,4,3],[3,4,4,4],[3,6,3,7],[3,8,3,9],[3,12,4,12],[3,13,4,13],[1,1,1,15],[3,5,4,5],[3,10,3,11],[3,14,3,16]],"flags":["formulas_cached_only"]}
[]
[null,"장비사양표(냉난방 실내기)"]
[]
["분류","평형","제품명","사양","단위","수량","용량(KW)",null,"소비전력(KW)",null,"운전전류(A)",null,"전원선(㎟)","통신선(㎟)","접속구경(mm)"]
[{"$nulls":6},"냉방능력","난방능력","냉방","난방","냉방","난방",null,null,"액관","가스관","드레인관"]
["실내기","10평형","R-W0400T2S","4WAY","대",1,4,4.5,0.03,0.03,0.22,0.22,2.5,"1.0~1.5",9.52,15.88,32]
[null,"13평형","R-W0520T2S",null,"대",1,5.2,5.9,0.03,0.03,0.22,0.22,2.5,"1.0~1.5",9.52,15.88,32]
[null,"15평형","R-W0600T2S",null,"대",1,6,6.8,0.03,0.03,0.22,0.22,2.5,"1.0~1.5",9.52,15.88,32]
[null,"18평형","R-W0720T2S",null,"대",1,7.2,8.1,0.07,0.07,0.6,0.6,2.5,"1.0~1.5",9.52,15.88,32]
[null,"21평형","R-W0830T2S",null,"대",1,8.3,9.3,0.07,0.07,0.6,0.6,2.5,"1.0~1.5",9.52,15.88,32]
[null,"25평형","R-W1000T2S",null,"대",1,10,11.2,0.07,0.07,0.6,0.6,2.5,"1.0~1.5",9.52,15.88,32]
[null,"27평형","R-W1100T2S",null,"대",1,11,12.4,0.09,0.09,0.77,0.77,2.5,"1.0~1.5",9.52,15.88,32]
[null,"33평형","R-W1300T2S",null,"대",1,13,14.6,0.1,0.1,0.8,0.8,2.5,"1.0~1.5",9.52,15.88,32]
[null,"36평형","R-W1450T2S",null,"대",1,14.5,16.3,0.12,0.12,0.96,0.96,2.5,"1.0~1.5",9.52,15.88,32]
[null,"13평형","R-W0521G2S","2WAY","대",1,5.2,5.9,0.02,0.02,0.24,0.24,2.5,"1.0~1.5",6.35,12.7,32]
[null,"15평형","R-W0601G2S",null,"대",1,6,6.8,0.02,0.02,0.25,0.25,2.5,"1.0~1.5",9.52,15.88,32]
[null,"18평형","R-W0721G2S",null,"대",1,7.2,8.1,0.03,0.03,0.3,0.3,2.5,"1.0~1.5",9.52,15.88,32]
[null,"5평형","R-W0200C2S","1WAY","대",1,2,2.2,0.01,0.01,0.05,0.05,2.5,"1.0~1.5",6.35,12.7,32]
[null,"6평형","R-W0230C2S",null,"대",1,2.3,2.6,0.02,0.02,0.09,0.09,2.5,"1.0~1.5",6.35,12.7,32]
[null,"8평형","R-W0320C2S",null,"대",1,3.2,3.6,0.02,0.02,0.09,0.09,2.5,"1.0~1.5",6.35,12.7,32]
[null,"10평형","R-W0400C2S",null,"대",1,4,4.5,0.03,0.03,0.14,0.14,2.5,"1.0~1.5",6.35,12.7,32]
[null,"13평형","R-W0520C2S",null,"대",1,5.2,5.9,0.03,0.03,0.14,0.14,2.5,"1.0~1.5",6.35,12.7,32]
[null,"15평형","R-W0600C2S",null,"대",1,6,6.8,0.04,0.04,0.18,0.18,2.5,"1.0~1.5",9.52,15.88,32]
[null,"18평형","R-W0720C2S",null,"대",1,7.2,7.2,0.05,0.05,0.23,0.23,2.5,"1.0~1.5",9.52,15.88,32]
[null,"13평형","RNW0520B2S","매립덕트형","대",1,5.2,5.9,0.15,0.15,1.06,1.06,2.5,"1.0~1.5",6.35,12.7,32]
[null,"15평형","RNW0600B2S",null,"대",1,6,6.8,0.15,0.15,1.06,1.06,2.5,"1.0~1.5",9.52,15.88,32]
[null,"18평형","RNW0720B2S",null,"대",1,7.2,8.1,0.15,0.15,1.06,1.06,2.5,"1.0~1.5",9.52,15.88,32]
[null,"21평형","RNW0830B2S",null,"대",1,8.3,9.3,0.25,0.25,2.65,2.65,2.5,"1.01~1.5",9.52,15.88,32]
[null,"6평형","RNW0230R2S","벽걸이형","대",1,2.3,2.6,0.03,0.03,0.25,0.25,2.5,"1.0~1.5",6.35,12.7,20]
[null,"8평형","RNW0320R2S",null,"대",1,3.2,3.6,0.03,0.03,0.25,0.25,2.5,"1.0~1.5",6.35,12.7,20]
[null,"10평형","RNW0400R2S",null,"대",1,4,4.5,0.03,0.03,0.25,0.25,2.5,"1.0~1.5",6.35,12.7,20]
[null,"13평형","RNW0520R2S",null,"대",1,5.2,5.9,0.05,0.05,0.52,0.52,2.5,"1.0~1.5",6.35,12.7,20]
[null,"36평형","RNW1450P2S","상업용스텐드","대",1,14.5,16.3,0.25,0.25,1.3,1.3,2.5,"1.0~1.5",9.52,15.88,19]
[null,"73평형","RNW2900P2S",null,"대",1,29,32.6,0.4,0.4,2.3,2.3,4,"1.0~1.5",9.52,15.88,19]

{"sheet":"싱글형","index":1,"n_rows":25,"n_cols":21,"rows_kept":25,"cut":false,"hidden":false,"merged":[[3,14,4,14],[3,15,4,15],[3,16,3,17],[3,18,3,20],[3,13,4,13],[3,12,4,12],[1,1,1,19],[3,0,4,0],[3,1,4,1],[3,2,4,2],[3,3,4,3],[3,4,4,4],[3,5,4,5],[3,6,3,7],[3,8,3,9],[3,10,3,11]],"flags":["formulas_cached_only"]}
[]
[null,"장비사양표(냉난방 싱글형)"]
[]
["분류","평형","제품명","사양","단위","수량","용량(KW)",null,"소비전력(KW)",null,"운전전류(A)",null,"효율(APF)","전원","전원선(㎟)","통신선(㎟)","누전차단기",null,"접속구경(mm)"]
[{"$nulls":6},"냉방능력","난방능력","냉방","난방","냉방","난방",{"$nulls":4},"규격(A)","수량(대)","액관","가스관","드레인관"]
["싱글형(세트)","15평형","TW0601P2S","싱글4WAY","SET",1,6,7.2,1.7,2.05,8,9.7,5.51,"1.2.220v.60hz","2.5*3C","1.0*4C",30,"2P",6.35,12.7,32]
[null,"18평형","TW0720P2S",null,"SET",1,7.2,8.6,2.1,2.7,9.5,12.3,5.25,"1.2.220v.60hz","4.0*3C","1.0*4C",30,"2P",9.52,15.88,32]
[null,"23평형","TW0900M2S",null,"SET",1,9,11,2.9,3.5,13.2,15.9,5.53,"1.2.220v.60hz","4.0*3C","1.0*4C",30,"2P",9.52,15.88,32]
[null,"25평형","TW1001M2SR",null,"SET",1,10,12.9,2.6,3.3,11.8,15,6.1,"1.2.220v.60hz","6.0*3C","1.0*4C",40,"2P",9.52,15.88,32]
[null,"28평형","TW1101M2SR",null,"SET",1,11,13.2,3.05,3.55,13.9,16.1,6.03,"1.2.220v.60hz","6.0*3C","1.0*4C",40,"2P",9.52,15.88,32]
[null,"33평형","TW1301M2SR",null,"SET",1,13,15,3.9,4.1,17.7,18.6,5.84,"1.2.220v.60hz","6.0*3C","1.0*4C",40,"2P",9.52,15.88,32]
[null,"28평형","TW1101M9SR",null,"SET",1,11,13.2,3,3.5,4.6,5.4,6.11,"3.4.380v.60hz","2.5*5c","1.0*4c",20,"4p",9.52,15.88,32]
[null,"33평형","TW1301M9SR",null,"SET",1,13,15,3.7,4,5.7,6.1,5.85,"3.4.380v.60hz","2.5*5c","1.0*4c",20,"4p",9.52,15.88,32]
[null,"36평형","TW1451M9SR",null,"SET",1,14.5,16.7,4.6,4.9,7.2,7.4,5.55,"3.4.380v.60hz","2.5*5c","1.0*4c",20,"4p",9.52,15.88,32]
[null,"15평형","TW0600S2S","싱글2WAY","SET",1,6,7.2,2.05,2.65,9.3,12.1,4.85,"1.2.220v.60hz","4.0*3C","1.0*4C",30,"2P",6.35,12.7,32]
[null,"18평형","TW0720S2S",null,"SET",1,7.2,8.1,2.6,3.2,11.8,14.5,4.75,"1.2.220v.60hz","4.0*3C","1.0*4C",30,"2P",9.52,15.88,32]
[null,"6평형","TW0230U2S","싱글1WAY","SET",1,2.3,2.8,0.6,0.7,2.7,3.2,5.9,"1.2.220v.60hz","2.5*3c","1.0*4c",20,"2p",6.35,9.52,32]
[null,"8평형","TW0320U2S",null,"SET",1,3.2,3.6,0.9,1.1,4.1,5,5.73,"1.2.220v.60hz","2.5*3c","1.0*4c",20,"2p",6.35,9.52,32]
[null,"10평형","TW0400U2S",null,"SET",1,4,5,1.43,1.78,6.8,8.5,5.25,"1.2.220v.60hz","2.5*3c","1.0*4c",20,"2p",6.35,12.7,32]
[null,"13평형","PW0521R2S","싱글스텐드형","SET",1,5.2,6,1.5,1.65,6.8,7.5,5.85,"1.2.220v.60hz","2.5*3c","1.0*4c",20,"2p",6.35,12.7,32]
[null,"15평형","PW0601R2S",null,"SET",1,6,7.2,1.8,2.2,8.2,10,5.44,"1.2.220v.60hz","2.5*3c","1.0*4c",20,"2p",6.35,12.7,32]
[null,"18평형","PW0721R2S",null,"SET",1,7.2,8.5,2.15,2.3,9.8,10.5,5.57,"1.2.220v.60hz","4.0*3c","1.0*4c",30,"2p",9.52,15.88,32]
[null,"21평형","PW0831R2S",null,"SET",1,8.3,9.2,2.85,2.85,13,13,5.27,"1.2.220v.60hz","4.0*3c","1.0*4c",30,"2p",9.52,15.88,32]
[null,"28평형","PW1101T2SR",null,"SET",1,11,13.2,3,3.45,13.6,15.7,5.56,"1.2.220v.60hz","6.0*3c","1.0*4c",40,"2p",9.52,15.88,32]
[null,"28평형","PW1101T9SR",null,"SET",1,11,13.2,3,3.45,5.1,5.8,5.47,"3.4.380v.60hz","2.5*5c","1*4c",20,"4p",9.52,15.88,32]

{"sheet":"실외기","index":2,"n_rows":33,"n_cols":21,"rows_kept":33,"cut":false,"hidden":false,"merged":[[3,19,3,20],[3,6,3,8],[3,13,4,13],[3,14,4,14],[3,12,4,12],[3,9,3,11],[1,1,1,20],[3,0,4,0],[3,1,4,1],[3,2,4,2],[3,3,4,3],[3,4,4,4],[3,5,4,5],[3,15,4,15],[3,16,4,16],[3,17,3,18]],"flags":["formulas_cached_only"]}
[]
[null,"장비사양표(냉난방 멀티 실외기)"]
[]
["분류","평형","제품명","사양","단위","수량","용량(KW)",null,null,"소비전력(KW)",null,null,"운전전류","전원","냉난방효율(EERa)","전원선(㎟)","통신선(㎟)","누전차단기",null,"접속구경(mm)"]
[{"$nulls":6},"냉방능력","난방능력","난방저온","통합냉방","통합난방","난방저온",{"$nulls":5},"규격(A)","수량(대)","액관","가스관"]
["실외기","58평형","RPUW08EX9H","멀티V실외기","대",1,23.3,25.9,25.6,1.4,1.7,12,18,"3.4.380V.60Hz",7.23,2.5,"1.0~1.5",20,1,9.52,19.05]
[null,"58평형","RPUW081X9H",null,"대",1,23.3,25.9,23,2.1,9.2,13,18,"3.4.380V.60Hz",5.74,2.5,"1.0~1.5",20,1,9.52,19.05]
[null,"73평형","RPUW101X9H",null,"대",1,29.2,32.8,28,2.6,10.4,14.5,22.7,"3.4.380V.60Hz",5.56,4,"1.0~1.5",30,1,9.52,22.2]
[null,"87평형","RPUW121X9H",null,"대",1,34.8,39.2,32.5,2.6,11.6,14.5,24.8,"3.4.380V.60Hz",6.12,4,"1.0~1.5",30,1,12.7,28.58]
[null,"101평형","RPUW14EX9H",null,"대",1,40.6,45.7,35.8,3.1,13.6,17.5,34.5,"3.4.380V.60Hz",5.96,6,"1.0~1.5",40,1,12.7,28.58]
[null,"116평형","RPUW161X9H",null,"대",1,46.4,52.2,46.1,3.7,17.9,20.9,34.9,"3.4.380V.60Hz",5.88,6,"1.0~1.5",40,1,12.7,28.58]
[null,"130평형","RPUW181X9H",null,"대",1,52.2,56.7,51,4.1,21,25.5,39.9,"3.4.380V.60Hz",5.57,10,"1.0~1.5",50,1,15.88,28.58]
[null,"142평형","RPUW201X9H",null,"대",1,57,63,57,4.5,22.5,29.5,46.2,"3.4.380V.60Hz",5.82,10,"1.0~1.5",50,1,15.88,28.58]
[null,"160평형","RPUW221X9H",null,"대",1,64,72,58.5,5.3,25.2,32,50.1,"3.4.380V.60Hz",5.6,10,"1.0~1.5",60,1,15.88,28.58]
[null,"169평형","RPUW241X9H",null,"대",1,67.5,74,60,5.9,26,34,53.3,"3.4.380V.60Hz",5.31,10,"1.0~1.5",60,1,15.88,34.9]
[null,"189평형","RPUW261X9H",null,"대",1,75.6,85,72.5,7.5,27.9,40,62.7,"3.4.380V.60Hz",null,16,"1.0~1.5",75,1,19.05,34.9]
[null,"189평형","RP-W261X9H",null,"대",1,75.4,84.9,68.3,5.7,25.2,32,59.3,"3.4.380V.60Hz",null,16,"1.0~1.5",75,1,19.05,34.9]
[null,"203평형","RP-W281X9H",null,"대",1,81.2,91.4,71.6,6.2,27.2,35,69,"3.4.380V.60Hz",null,16,"1.0~1.5",75,1,19.05,34.9]
[null,"218평형","RP-W301X9H",null,"대",1,87,97.9,81.9,6.8,31.5,38.4,69.4,"3.4.380V.60Hz",null,16,"1.0~1.5",75,1,19.05,34.9]
[null,"232평형","RP-W321X9H",null,"대",1,92.8,102.4,86.8,7.2,34.6,43,74.4,"3.4.380V.60Hz",null,25,"1.0~1.5",100,1,19.05,34.9]
[null,"270평형","RP-W381X9H",null,"대",1,108.1,119.7,95.8,9,39.6,51.5,87.8,"3.4.380V.60Hz",null,25,"1.0~1.5",100,1,19.05,41.3]
[null,"299평형","RP-W421X9H",null,"대",1,119.7,130.7,111,10,47,59.5,93.2,"3.4.380V.60Hz",null,50,"1.0~1.5",125,1,19.05,41.3]
[null,"329평형","RP-W461X9H",null,"대",1,131.5,146,118.5,11.2,51.2,66,103.4,"3.4.380V.60Hz",null,50,"1.0~1.5",125,1,19.05,41.3]
[null,"357평형","RP-W501X9H",null,"대",1,142.9,158.9,128.3,11.6,51.2,66,112.6,"3.4.380V.60Hz",null,50,"1.0~1.5",125,1,19.05,41.3]
["실외기","28평형","RPUW040S2S","멀티V상업용","대",1,11,12.4,null,2.68,2.88,null,26,"1.2.220V.60Hz","4.1/4.31",4,"1.0~1.5",30,1,9.52,15.88]
[null,"36평형","RPUW050S2S",null,"대",1,14.5,16.3,null,3.5,3.58,null,26,"1.2.220V.60Hz","4.14/4.55",4,"1.0~1.5",30,1,9.52,15.88]
[null,"40평형","RPUW060S2S",null,"대",1,16,18,null,4.1,4.1,null,26,"1.2.220V.60Hz","3.9/4.4",6,"1.0~1.5",40,1,9.52,19.05]
[null,"28평형","RPUW040S9S",null,"대",1,11,12.4,null,2.5,2.7,null,14,"3.4.380v.60hz","4.4/4.59",2.5,"1.0~1.5",20,1,9.52,15.88]
[null,"36평형","RPUW050S9S",null,"대",1,14.5,16.3,null,3.5,3.6,null,14,"3.4.380v.60hz","4.14/4.53",2.5,"1.0~1.5",20,1,9.52,15.88]
[null,"40평형","RPUW060S9S",null,"대",1,16,18,null,4.1,4.09,null,14,"3.4.380v.60hz","3.9/4.4",2.5,"1.0~1.5",20,1,9.52,19.05]
[null,"56평형","RPUW080S9S",null,"대",1,22.4,25.2,null,7.47,6.4,null,21,"3.4.380v.60hz","3/3.94",4,"1.0~1.5",30,1,9.52,19.05]
[null,"70평형","RPUW100S9S",null,"대",1,28,31.5,null,10,8.4,null,25,"3.4.380v.60hz","3.8/3.75",6,"1.0~1.5",40,1,9.52,22.2]
[null,"84평형","RPUW120S9S",null,"대",1,33.6,37.8,null,9.81,9.75,null,28,"3.4.380v.60hz","3.43/3.88",6,"1.0~1.5",40,1,12.7,28.58]

{"sheet":"냉방전용","index":3,"n_rows":22,"n_cols":20,"rows_kept":22,"cut":false,"hidden":false,"merged":[[1,1,1,18],[3,0,4,0],[3,1,4,1],[3,2,4,2],[3,3,4,3],[3,4,4,4],[3,5,4,5],[3,6,3,7],[3,8,3,9],[3,10,4,10],[3,11,4,11],[3,12,4,12],[3,13,4,13],[3,14,4,14],[3,15,3,16],[3,17,3,19]],"flags":["formulas_cached_only"]}
[]
[null,"장비사양표(냉방전용)"]
[]
["분류","평형","제품명","사양","단위","수량","용량(KW)",null,"소비전력(KW)",null,"운전전류","전원","냉방효율(CSPF)","전원선(㎟)","통신선(㎟)","누전차단기",null,"접속구경(mm)"]
[{"$nulls":6},"냉방능력","난방능력","통합냉방","통합난방",{"$nulls":5},"규격(A)","수량(대)","액관","가스관","드레인관"]
["실외기","58평형","RPUQ080X9S","냉방전용","대",1,23,null,5.14,null,8.22,"3.4.380v.60hz",4.1,"10*5","(1~1.5)*2",40,1,12.7,28.58]
[null,"101평형","RPUQ140X9S",null,"대",1,40.6,null,10.26,null,16.41,"3.4.380v.60hz",3.96,"10*5","(1~1.5)*2",30,1,12.7,28.58]
[null,"142평형","RPUQ200X9S",null,"대",1,57,null,14.2,null,22.72,"3.4.380v.60hz",4.01,"10*5","(1~1.5)*2",50,1,15.88,28.58]
["상업용(실외기)","28평형","LRP-V1102M","냉방전용","대",1,11,null,2.8,null,22,"1.2.220v.60hz",3.93,4,"1.0~1.5",30,1,9.52,15.88]
[null,"40평형","LRP-V1602M",null,"대",1,16,null,4.2,null,25,"1.2.220v.60hz",3.81,6,"1.0~1.5",40,1,9.52,19.05]
[null,"58평형","RPUQ080S9S",null,"대",1,23,null,6.05,null,17,"3.4.380v.60hz",3.8,4,"1.0~1.5",30,1,9.52,19.05]
["싱글형 냉방기","15평형","TQ0600P2S","4WAY","SET",1,6,null,1.78,null,13,"1.2.220v.60hz",7.56,"2.5*3C","1.0*5c",20,"2p",6.35,12.7,32]
[null,"18평형","LTQ720SN",null,"SET",1,7.2,null,1.95,null,14,"1.2.220v.60hz",6.93,"2.5*3C","1.0*5c",25,"2p",9.52,15.88,32]
[null,"33평형","LTQ1300SM",null,"SET",1,13,null,4.6,null,25,"1.2.220v.60hz",6.14,"6*3c","1*5c",40,"2p",9.52,15.88,32]
[null,"6평형","TQ230G2S","1WAY","SET",1,2.3,null,0.81,null,7,"1.2.220v.60hz",4.4,"2.5*3c","1.0*4c",15,"2p",6.35,9.52,32]
[null,"8평형","LTQ322SU",null,"SET",1,3.2,null,1,null,7.7,"1.2.220v.60hz",5.35,"2.5*3c","1.0*4c",15,"2p",6.35,9.52,32]
[null,"10평형","LTQ400SUZ",null,"SET",1,4,null,1.12,null,13,"1.2.220v.60hz",6.12,"2.5*3c","1.0*4c",20,"2p",6.35,12.7,32]
["싱글형스텐드","25평형","LPQ1000VP","스텐드형","SET",1,10,null,3.2,null,23,"1.2.220v.60hz",5.506,"4*3c","1*5c",30,"2p",9.52,15.88,16]
[null,"33평형","LPQ1300VP",null,"SET",1,13,null,4.6,null,27,"1.2.220v.60hz",6.111,"6*3c","1*5c",40,"2p",9.52,15.88,16]
[null,"21평형","PQ0830R2SF",null,"SET",1,8.3,null,2.8,null,19,"1.2.220v.60hz",5.31,"4*3c","1*4c",30,"2p",9.52,15.88,16]
[null,"33평형","PQ1301T2SF",null,"SET",1,13,null,4.3,null,29,"1.2.220v.60hz",4.96,"6*3c","1.0*4c",40,"2p",9.52,15.88,19]
[null,"58평형","PQ2300F9SF",null,"SET",1,23,null,8.2,null,31,"3.4.380v.60hz",null,"6*5c","1.5*4c",40,"4p",9.52,22.22,19]

{"sheet":"설치비","index":4,"n_rows":121,"n_cols":8,"rows_kept":121,"cut":false,"hidden":false,"merged":[[1,0,1,7]],"flags":["formulas_cached_only"]}
[]
["설 치 비(시공비)"]
[]
["분류","모델명","규격","단위","수량","단가","금액","비고"]
["실내기","R-W0400T2S","4WAY","대",1]
[null,"R-W0520T2S",null,"대",1]
[null,"R-W0600T2S",null,"대",1]
[null,"R-W0720T2S",null,"대",1]
[null,"R-W0830T2S",null,"대",1]
[null,"R-W1000T2S",null,"대",1]
[null,"R-W1100T2S",null,"대",1]
[null,"R-W1300T2S",null,"대",1]
[null,"R-W1450T2S",null,"대",1]
[null,"R-W0521G2S","2WAY","대",1]
[null,"R-W0601G2S",null,"대",1]
[null,"R-W0721G2S",null,"대",1]
[null,"R-W0200C2S","1WAY","대",1]
[null,"R-W0230C2S",null,"대",1]
[null,"R-W0320C2S",null,"대",1]
[null,"R-W0400C2S",null,"대",1]
[null,"R-W0520C2S",null,"대",1]
[null,"R-W0600C2S",null,"대",1]
[null,"R-W0720C2S",null,"대",1]
[null,"RNW0520B2S","매립덕트형","대",1]
[null,"RNW0600B2S",null,"대",1]
[null,"RNW0720B2S",null,"대",1]
[null,"RNW0830B2S",null,"대",1]
[null,"RNW0230R2S","벽걸이형","대",1]
[null,"RNW0320R2S",null,"대",1]
[null,"RNW0400R2S",null,"대",1]
[null,"RNW0520R2S",null,"대",1]
[null,"RNW1450P2S","상업용스텐드","대",1]
[null,"RNW2900P2S",null,"대",1]
["실외기","RPUW08EX9H","멀티V실외기","대",1]
[null,"RPUW081X9H",null,"대",1]
[null,"RPUW101X9H",null,"대",1]
[null,"RPUW121X9H",null,"대",1]
[null,"RPUW14EX9H",null,"대",1]
[null,"RPUW16EX9H",null,"대",1]
[null,"RPUW181X9H",null,"대",1]
[null,"RPUW201X9H",null,"대",1]
[null,"RPUW221X9H",null,"대",1]
[null,"RPUW241X9H",null,"대",1]
[null,"RPUW261X9H",null,"대",1]
[null,"RP-W261X9H",null,"대",1]
[null,"RP-W281X9H",null,"대",1]
[null,"RP-W301X9H",null,"대",1]
[null,"RP-W321X9H",null,"대",1]
[null,"RP-W381X9H",null,"대",1]
[null,"RP-W421X9H",null,"대",1]
[null,"RP-W461X9H",null,"대",1]
[null,"RP-W501X9H",null,"대",1]
[null,"RPUW040S2S","멀티V상업용","대",1]
[null,"RPUW050S2S",null,"대",1]
[null,"RPUW060S2S",null,"대",1]
[null,"RPUW040S9S",null,"대",1]
[null,"RPUW050S9S",null,"대",1]
[null,"RPUW060S9S",null,"대",1]
[null,"RPUW080S9S",null,"대",1]
[null,"RPUW100S9S",null,"대",1]
[null,"RPUW120S9S",null,"대",1]
["싱글형","TW0601P2S","싱글4WAY","SET",1]
[null,"TW0720P2S",null,"SET",1]
[null,"TW0900M2S",null,"SET",1]
[null,"TW1001M2SR",null,"SET",1]
[null,"TW1101M2SR",null,"SET",1]
[null,"TW1301M2SR",null,"SET",1]
[null,"TW1101M9SR",null,"SET",1]
[null,"TW1301M9SR",null,"SET",1]
[null,"TW1451M9SR",null,"SET",1]
[null,"TW0600S2S","싱글2WAY","SET",1]
[null,"TW0720S2S",null,"SET",1]
[null,"TW0230U2S","싱글1WAY","SET",1]
[null,"TW0320U2S",null,"SET",1]
[null,"TW0400U2S",null,"SET",1]
[null,"PW0521R2S","싱글스텐드형","SET",1]
[null,"PW0601R2S",null,"SET",1]
[null,"PW0721R2S",null,"SET",1]
[null,"PW0831R2S",null,"SET",1]
[null,"PW1101T2SR",null,"SET",1]
[null,"PW1101T9SR",null,"SET",1]
["실외기","RPUQ080X9S","냉방전용","대",1]
[null,"RPUQ140X9S",null,"대",1]
[null,"RPUQ200X9S",null,"대",1]
["상업용실외기","LRP-V1102M","냉방전용","대",1]
[null,"LRP-V1602M",null,"대",1]
[null,"RPUQ080S9S",null,"대",1]
["싱글용","TQ0600P2S","4WAY","SET",1]
[null,"LTQ720SN",null,"SET",1]
[null,"LTQ1300SM",null,"SET",1]
[null,"TQ230G2S","1WAY","SET",1]
[null,"LTQ322SU",null,"SET",1]
[null,"LTQ400SUZ",null,"SET",1]
["싱글스텐드","LPQ1000VP","스텐드형","SET",1]
[null,"LPQ1300VP",null,"SET",1]
[null,"PQ0830R2SF",null,"SET",1]
[null,"PQ1301T2SF",null,"SET",1]
[null,"PQ2300F9SF",null,"SET",1]
["설치비"]
[null,"멀티브이 설치","설치비","식",1]
[null,"냉매배관",6.35,"M",1]
[null,"냉매배관",9.52,"M",1]
[null,"냉매배관",12.7,"M",1]
[null,"냉매배관",15.88,"M",1]
[null,"냉매배관",19.05,"M",1]
[null,"냉매배관",28.58,"M",1]
[null,"냉매배관",34.9,"M",1]
[null,"냉매배관",41.3,"M",1]
[null,"드레인배관",32,"M",1]
[null,"드레인배관",20,"M",1]
[null,"분지관",null,"EA",1]
[null,"냉매 ","R410","kg",1]
[null,"통신선",null,"M",1]
[null,"통신선설치",null,"식",1]
[null,"리모컨설치",null,"식",1]
[null,"유선리모컨",null,"EA",1]
[null,"배관마감","배관커버","M",1]
[null,"천공","코아작업","식",1]
[null,"실외기받침대",null,"EA",1]
[null,"실외기기초","패드","EA",1]
[null,"장비사용료","크레인","식",1]